## V360_softening_replacement
V360 OBS
Suitable replacements
Possible replacements if higher pressure drop is acceptable
SIMPLEX VALVE SINGLE COLUMN
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | Service flow rate @ 1.5 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out | Tank size @BV 40 | 24" |  |  | 30" | [6 empty] | 36" | [8 empty] | 42"
[7 empty] | Liters of resin | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500 | 525 | 550 | 575 | 600 | 625 | 650 | 675 | 700 | 725 | 750 | 775 | 800
[7 empty] | Service flow rate m3/h | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 40 | 42 | 44 | 48 | 50 | 55 | 57 | 60
Siata | V360 | 32 |  | 15 | SM | 3" flange + several choices | bar: 12 to 32
Autotrol | 298 IT | 18.2 | 22.3 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 22
Siata | V250 | 21 | 25.7 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: 12 to 26
Fleck | 3150 | 22 | 26.9 | 24 | TM/SM | 2" BSP female | bar: 12 to 27
Fleck | 2910 | 24 | 29.4 | 7.9 | TM/SM | 2" BSP female | bar: 12 to 29
Autotrol | 288IT* | 36 | 44.1 | 20.2 | SM | 2"BSP male SS - other connection kit also available | bar: 12 to 44
Fleck | 3900 | 57 | 69.8 | 24 | TM/SM | 3" BSP female
DUPLEX PARALLEL | [6 empty] | Tank size for duplex | 12: 2x16"; 13: 2x'18"; 17: 2x21; 21: 2x'24"; 29: 2x'30"
Autotrol | 298 IT | 36.4 | 44.6 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 44
Siata | V250 | 42 | 51.4 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld
Fleck | 2910 | 48 | 58.8 | 7.9 | TM/SM | 2" BSP female
TRIPLEX PARALLEL | [6 empty] | Tank size for triplex | 12: 3x14; 15: 3x16; 17: 3x18; 25: 3x21; 31: 3x24
Fleck | 2850 | 34.8 | 42.6 | 11.1 | TM/SM | 1 ½" BSP female | bar: 12 to 42
*Magnum with flow booster based on 3V50 valves
DUPLEX ALTERNATING V360
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | Service flow rate @ 1.5 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out | Tank size @BV 40 | 12: 24"; 15: 30"; 22: 36"; 31: 42"
[7 empty] | Liters of resin | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500 | 525 | 550 | 575 | 600 | 625 | 650 | 675 | 700 | 725 | 750 | 775 | 800
[7 empty] | Service flow rate m3/h | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 40 | 42 | 44 | 48 | 50 | 55 | 57 | 60
Siata | V360 | 32 |  | 15 | SM | 3" flange + several choices | bar: 12 to 32
Autotrol | 298 IT | 18.2 | 22.3 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 22
Siata | V250 | 21 | 25.7 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: 12 to 26
Fleck | 3150 | 22 | 26.9 | 24 | TM/SM | 2" BSP female | bar: 12 to 27
Fleck | 2910 | 24 | 29.4 | 7.9 | TM/SM | 2" BSP female | bar: 12 to 29
Autotrol | 288IT* | 36 | 44.1 | 20.2 | SM | 2"BSP male SS - other connection kit also available | bar: 12 to 44
Fleck | 3900 | 57 | 69.8 | 24 | TM/SM | 3" BSP female
TRIPLEX SYSTEM 9 | [6 empty] | Tank size for tiplex | 12: 3x16"; 13: 3x'18"; 17: 3x 21"; 21: 3x'24"; 29: 3x'30"
Siata | V250 | 42 | 51.4 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld
Fleck | 2910 | 48 | 58.8 | 7.9 | TM/SM | 2" BSP female
TRIPLEX PARALLEL | [6 empty] | Tank size for tiplex | 12: 3x16"; 13: 3x'18"; 17: 3x 21"; 21: 3x'24"; 29: 3x'30"
Autotrol | 298 IT | 54.6 | 66.9 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 44
*Magnum with flow booster based on 3V50 valves | bar: 12 to 44
DUPLEX PARALLEL SYSTEM V360
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | Service flow rate @ 1.5 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out | Tank size @BV 40 | 12: 2x'24"; 15: 30"; 22: 36"; 31: 42"
[7 empty] | Liters of resin | 2x300 | 2x325 | 2x350 | 2x375 | 2x400 | 2x425 | 2x450 | 2x475 | 2x500 | 2x525 | 2x550 | 2x575 | 2x600 | 2x625 | 2x650 | 2x675 | 2x700 | 2x725 | 2x750 | 2x775 | 2x800
[7 empty] | Service flow rate m3/h | 24 (2x12) | 26 (2x13) | 28 (2x16) | 30 (2x15) | 32 (2x16) | 34 (2x17) | 36 (2x18) | 38 (2x19) | 40 (2x20) | 42 (2x21) | 44 (2x22) | 46 (2x23) | 48 (2x24) | 50 (2x25) | 52 (2x26) | 54 (2x27) | 56 (2x28) | 58 (2x29) | 60 (2x30) | 62 (2x31) | 64 (2x32) | 66 | 68 | 70 | 72 | 73 | 80 | 114
Siata | V360 | 64 |  | 15 | SM | 3" flange + several choices
Autotrol | 298 IT | 36.4 | 44.6 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 22
Siata | V250 | 42 | 51.4 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: 12 to 25
Fleck | 3150 | 44 | 53.9 | 24 | TM/SM | 2" BSP female | bar: 12 to 27
Fleck | 2910 | 48 | 58.8 | 7.9 | TM/SM | 2" BSP female | bar: 12 to 29
Autotrol | 288IT* | 72 | 88.2 | 20.2 | SM | 2"BSP male SS - other connection kit also available | bar: 12 to 42
Fleck | 3900 | 114 | 139.6 | 24 | TM/SM | 3" BSP female | bar: 12 to 44
TRIPLEX SYSTEM 6 | [6 empty] | Tank size for tiplex | 12: 3x18"; 13: 3x21"; 16: 3x24"; 23: 3x30"
Autotrol | 298 IT | 54.6 | 66.9 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 33
Siata | V250 | 63 | 77.2 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: 12 to 40
Fleck | 2910 | 72 | 88.2 | 7.9 | TM/SM | 2" BSP female | bar: 12 to 42
QUADPLEX PARALLEL | [6 empty] | Tank size for quadplex | 12: 4x18"; 17: 4x21"; 21: 4x24"; 30: 4x30"
Fleck | 2850 | 46.4 | 56.8 | 11.1 | TM/SM | 1 ½" BSP female | bar: 12 to 28
Autotrol | 298 IT | 72.8 | 89.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: 12 to 42
*Magnum with flow booster based on 3V50 valves

## V363_V350_V360_replacement
V360, V363, V351, V350 OBS
Possible replacement
Higher flow rate for Side Mount (SM)
FILTER VALVE V351 | [6 empty] | Backwash flow rate m3/h
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Siata | V351 | 23 | 29 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 29
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 20
Fleck | 3150 | 22 (23**) | 24 (25**) | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 25
Fleck | 3900 | 57 | 24 | TM/SM | 3" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 24
Siata | 3V-50 | 23.4 | 33 | SM valve nest pipping | D.50 mm to be glued, 1 1/2" & 2” male, 1 ½” female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 33
Siata | 3V-63 | 24 | 44 | SM valve nest pipping | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
Autotrol | 293 IT* | 18.2 | 44 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
*Magnum with flow booster based on 3V63 valves
FILTER VALVE V350 | [6 empty] | Backwash flow rate m3/h 1: Backwash flow rate m3/h
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Siata | V350 | 23 | 31 | SM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 31
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 20
Fleck | 3150 | 22 (23**) | 24 (25**) | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 25
Fleck | 3900 | 57 | 24 | TM/SM | 3" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 24
Siata | 3V-50 | 23.4 | 33 | SM valve nest pipping | D.50 mm to be glued, 1 1/2" & 2” male, 1 ½” female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 33
Siata | 3V-63 | 24 | 44 | SM valve nest pipping | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
Autotrol | 293 IT* | 18.2 | 44 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
*Magnum with flow booster based on 3V63 valves
FILTER VALVE V363 | [6 empty] | Backwash flow rate m3/h 1: Backwash flow rate m3/h
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Siata | V363 | 36 | 54 | SM | 63 mm PVC, 2" PVC
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 20
Fleck | 3150 | 22 (23**) | 24 (25**) | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 25
Fleck | 3900 | 57 | 24 | TM/SM | 3" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 24
Siata | 3V-50 | 23.4 | 33 | SM valve nest pipping | D.50 mm to be glued, 1 1/2" & 2” male, 1 ½” female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 33
Siata | 3V-63 | 24 | 44 | SM valve nest pipping | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
Autotrol | 293 IT* | 18.2 | 44 | TM/SM | 2"BSP male SS valve - other connection kit also available and 63mmOD piping | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
*Magnum with flow booster based on 3V63 valves
FILTER VALVE V360F | [6 empty] | Backwash flow rate m3/h 1: Backwash flow rate m3/h
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Siata | V360 | 32 | 15 | SM | 3" flange + several choices connectors | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 15
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 20
Fleck | 3150 | 22 (23**) | 24 (25**) | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 25
Fleck | 3900 | 57 | 24 | TM/SM | 3" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 24
Siata | 3V-50 | 23.4 | 33 | SM valve nest pipping | D.50 mm to be glued, 1 1/2" & 2” male, 1 ½” female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 33
Siata | 3V-63 | 24 | 44 | SM valve nest pipping | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
Autotrol | 293 IT* | 18.2 | 44 | TM/SM | 2"BSP male SS valve - other connection kit also available and 63mmOD piping | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 44
*Magnum with flow booster based on 3V63 valves
** BKW flow rate for SM
V360 OBS
V350 OBS
V351 OBS
V363 OBS
Possible suitable replacements
EXAMPLE: Sand filter
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out | Tank size | Backwash flow rate m3/h 1: 14"; Backwash flow rate m3/h 2: 16"; Backwash flow rate m3/h 3: 18"; Backwash flow rate m3/h 4: 21"; Backwash flow rate m3/h 5: 24"; Backwash flow rate m3/h 6: 30"; Backwash flow rate m3/h 7: 36"; Backwash flow rate m3/h 8: 42"; Backwash flow rate m3/h 9: 48"; Backwash flow rate m3/h 10: 55"; Backwash flow rate m3/h 11: 63"
[6 empty] | BKW flow rate m3/h @ 44 m3/h/m² | Backwash flow rate m3/h 1: 4.4; Backwash flow rate m3/h 2: 5.7; Backwash flow rate m3/h 3: 7.2; Backwash flow rate m3/h 4: 9.8; Backwash flow rate m3/h 5: 12.8; Backwash flow rate m3/h 6: 20.1; Backwash flow rate m3/h 7: 28.9; Backwash flow rate m3/h 8: 39.3; Backwash flow rate m3/h 9: 51.5
[6 empty] | Service flow rate m3/h @ 7.35 m3/h/m² | Backwash flow rate m3/h 1: 0.7; Backwash flow rate m3/h 2: 1; Backwash flow rate m3/h 3: 1.2; Backwash flow rate m3/h 4: 1.6; Backwash flow rate m3/h 5: 2.1; Backwash flow rate m3/h 6: 3.4; Backwash flow rate m3/h 7: 4.8; Backwash flow rate m3/h 8: 6.6; Backwash flow rate m3/h 9: 8.6; Backwash flow rate m3/h 10: 11.3; Backwash flow rate m3/h 11: 14.8
Siata | V360 | 32 | 15 | SM | 3" flange + several choices connectors | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 5
Siata | V350 | 23 | 31 | SM | '1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 7
Siata | V351 | 23 | 29 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 7
Siata | V363 | 36 | 54 | SM | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 8
Siata | V250 | 21 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 4
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 6
Fleck | 3150 | 22 | 24 | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 6
Siata | 3V-50 | 23.4 | 33 | SM valve nest pipping | D.50 mm to be glued, 1 1/2" & 2” male, 1 ½” female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 7
Siata | 3V-63 | 24 | 44 | SM valve nest pipping | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 8
DUPLEX PARALLEL | [5 empty] | Tank size for duplex | Backwash flow rate m3/h 3: 2x14"; Backwash flow rate m3/h 4: 2x16; Backwash flow rate m3/h 5: 2x18"; Backwash flow rate m3/h 6: 2x21; Backwash flow rate m3/h 7: 2x30"; Backwash flow rate m3/h 8: 2x30"
[6 empty] | BKW flow rate m3/h @ 44 m3/h/m² | Backwash flow rate m3/h 3: 4.4; Backwash flow rate m3/h 4: 5.7; Backwash flow rate m3/h 5: 7.2; Backwash flow rate m3/h 6: 9.8; Backwash flow rate m3/h 7: 20.1; Backwash flow rate m3/h 8: 20.1
[6 empty] | Service flow rate m3/h @ 7.35 m3/h/m² | Backwash flow rate m3/h 3: 1.4; Backwash flow rate m3/h 4: 2; Backwash flow rate m3/h 5: 2.4; Backwash flow rate m3/h 6: 3.2; Backwash flow rate m3/h 7: 6.8; Backwash flow rate m3/h 8: 6.8
Fleck | 2850 | 34.8 | 11.1 | TM/SM | 1 ½" BSP female |  | Backwash flow rate m3/h 1: SIMPLEX IS ENOUGH
Siata | V250 | 21 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 3 to Backwash flow rate m3/h 6
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 3 to Backwash flow rate m3/h 8
Fleck | 3150 | 22 | 24 | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 3 to Backwash flow rate m3/h 8
EXAMPLE: Granular Activated Carbon Filter
Brand | Model | Service flow rate @ 1 bar ∆P (m3/h) | BKW flow rate @ 1,7 bar ∆P (m3/h) | Mounting | In/Out | Tank size | Backwash flow rate m3/h 1: 14"; Backwash flow rate m3/h 2: 16"; Backwash flow rate m3/h 3: 18"; Backwash flow rate m3/h 4: 21"; Backwash flow rate m3/h 5: 24"; Backwash flow rate m3/h 6: 30"; Backwash flow rate m3/h 7: 36"; Backwash flow rate m3/h 8: 42"; Backwash flow rate m3/h 9: 48"; Backwash flow rate m3/h 10: 55"; Backwash flow rate m3/h 11: 63"
[6 empty] | BKW flow rate m3/h @ 22 m3/h/m² | Backwash flow rate m3/h 1: 2.2; Backwash flow rate m3/h 2: 2.9; Backwash flow rate m3/h 3: 3.6; Backwash flow rate m3/h 4: 4.9; Backwash flow rate m3/h 5: 6.4; Backwash flow rate m3/h 6: 10; Backwash flow rate m3/h 7: 14.4; Backwash flow rate m3/h 8: 19.7; Backwash flow rate m3/h 9: 25.7; Backwash flow rate m3/h 10: 33.7; Backwash flow rate m3/h 11: 44.2
[6 empty] | Service flow rate m3/h @ 7.35 m3/h/m² | Backwash flow rate m3/h 1: 0.7; Backwash flow rate m3/h 2: 1; Backwash flow rate m3/h 3: 1.2; Backwash flow rate m3/h 4: 1.6; Backwash flow rate m3/h 5: 2.1; Backwash flow rate m3/h 6: 3.4; Backwash flow rate m3/h 7: 4.8; Backwash flow rate m3/h 8: 6.6; Backwash flow rate m3/h 9: 8.6; Backwash flow rate m3/h 10: 11.3; Backwash flow rate m3/h 11: 14.8
Siata | V360 | 32 | 15 | SM | 3" flange + several choices connectors | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 7
Siata | V350 | 23 | 31 | SM | '1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 7
Siata | V351 | 23 | 29 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 9
Siata | V363 | 36 | 54 | SM | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 11
Siata | V250 | 21 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 6
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 8
Fleck | 3150 | 22 | 24 | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 8
Siata | 3V-50 | 23.4 | 33 | SM valve nest pipping | D.50 mm to be glued, 1 1/2" & 2” male, 1 ½” female | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 9
Siata | 3V-63 | 24 | 44 | SM valve nest pipping | 63 mm PVC, 2" PVC | bar: Backwash flow rate m3/h 1 to Backwash flow rate m3/h 11
DUPLEX PARALLEL | [5 empty] | Tank size for duplex | Backwash flow rate m3/h 3: 2x14"; Backwash flow rate m3/h 4: 2x16; Backwash flow rate m3/h 5: 2x18"; Backwash flow rate m3/h 6: 2x21; Backwash flow rate m3/h 7: 2x30"; Backwash flow rate m3/h 8: 2x30"; Backwash flow rate m3/h 9: 2x36"; Backwash flow rate m3/h 10: 2x42"; Backwash flow rate m3/h 11: 2x48"
[6 empty] | BKW flow rate m3/h @ 22 m3/h/m² | Backwash flow rate m3/h 3: 2.2; Backwash flow rate m3/h 4: 2.9; Backwash flow rate m3/h 5: 3.6; Backwash flow rate m3/h 6: 4.9; Backwash flow rate m3/h 7: 10; Backwash flow rate m3/h 8: 10; Backwash flow rate m3/h 9: 14.4; Backwash flow rate m3/h 10: 19.7; Backwash flow rate m3/h 11: 25.7
[6 empty] | Service flow rate m3/h @ 7.35 m3/h/m² | Backwash flow rate m3/h 3: 1.4; Backwash flow rate m3/h 4: 2; Backwash flow rate m3/h 5: 2.4; Backwash flow rate m3/h 6: 3.2; Backwash flow rate m3/h 7: 6.8; Backwash flow rate m3/h 8: 6.8; Backwash flow rate m3/h 9: 9.2; Backwash flow rate m3/h 10: 6.6; Backwash flow rate m3/h 11: 17.2
Fleck | 2850 | 34.8 | 11.1 | TM/SM | 1 ½" BSP female |  | Backwash flow rate m3/h 1: SIMPLEX IS ENOUGH
Siata | V250 | 21 | 12 | TM | 1 1/2" BSP male or female, 2" male BSP, OD 50 mm socket weld | bar: Backwash flow rate m3/h 3 to Backwash flow rate m3/h 8
Autotrol | 293 IT | 18.2 | 20.2 | TM/SM | 2"BSP male SS - other connection kit also available | bar: Backwash flow rate m3/h 3 to Backwash flow rate m3/h 10
Fleck | 3150 | 22 | 24 | TM/SM | 2" BSP female | bar: Backwash flow rate m3/h 3 to Backwash flow rate m3/h 10
Calculated BKW & Service flow rates upon media and tank size
[57 empty] | Tank size |  |  | 14" |  | 16" |  | 18" |  | 21" |  | 24" |  | 30" |  | 36" |  | 42" |  | 48" |  | 55" |  | 63"
[57 empty] | Tank area m2 |  |  | 0.099315 |  | 0.12972 |  | 0.16417 |  | 0.22346 |  | 0.29186 |  | 0.45604 |  | 0.65669 |  | 0.89383 |  | 1.1675 |  | 1.5328 |  | 2.0111
[57 empty] | Media | Backwash Velocity (m3/h/m² ) | Service Velocity (m3/h/m² ) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h) | BKW (m3/h) | Service (m3/h)
[57 empty] | Pyrolox | 66 | 12.25 | 6.5548 | 1.2166 | 8.5613 | 1.589 | 10.8354 | 2.0111 | 14.7482 | 2.7374 | 19.263 | 3.5753 | 30.0984 | 5.5864 | 43.3417 | 8.0445 | 58.9929 | 10.9494 | 77.052 | 14.3013 | 101.1641 | 18.7767 | 132.7341 | 24.6362
[57 empty] | Sand | 44 | 7.35 | 4.3698 | 0.72996 | 5.7076 | 0.95342 | 7.2236 | 1.2067 | 9.8322 | 1.6424 | 12.842 | 2.1452 | 20.0656 | 3.3519 | 28.8945 | 4.8267 | 39.3286 | 6.5697 | 51.368 | 8.5808 | 67.4428 | 11.266 | 88.4894 | 14.7817
[57 empty] | Multimedia | 36 | 26.95 | 3.5753 | 2.6765 | 4.6698 | 3.4959 | 5.9102 | 4.4245 | 8.0445 | 6.0222 | 10.5071 | 7.8657 | 16.4173 | 12.2902 | 23.6409 | 17.6979 | 32.178 | 24.0888 | 42.0283 | 31.4629 | 55.1804 | 41.3087 | 72.4004 | 54.1997
[57 empty] | Greensand | 31 | 4.9 | 3.0788 | 0.48664 | 4.0212 | 0.63561 | 5.0894 | 0.80445 | 6.9272 | 1.0949 | 9.0478 | 1.4301 | 14.1371 | 2.2346 | 20.3575 | 3.2178 | 27.7088 | 4.3798 | 36.1911 | 5.7205 | 47.5165 | 7.5107 | 62.3448 | 9.8545
[57 empty] | Birm | 26 | 8.57 | 2.5822 | 0.85113 | 3.3726 | 1.1117 | 4.2685 | 1.407 | 5.8099 | 1.915 | 7.5885 | 2.5013 | 11.857 | 3.9082 | 17.074 | 5.6279 | 23.2396 | 7.6601 | 30.3538 | 10.0051 | 39.8525 | 13.136 | 52.2892 | 17.2353
[57 empty] | GAC | 22 | 7.35 | 2.1849 | 0.72996 | 2.8538 | 0.95342 | 3.6118 | 1.2067 | 4.9161 | 1.6424 | 6.421 | 2.1452 | 10.0328 | 3.3519 | 14.4472 | 4.8267 | 19.6643 | 6.5697 | 25.684 | 8.5808 | 33.7214 | 11.266 | 44.2447 | 14.7817
[57 empty] | Antracite | 36 | 12.25 | 3.5753 | 1.2166 | 4.6698 | 1.589 | 5.9102 | 2.0111 | 8.0445 | 2.7374 | 10.5071 | 3.5753 | 16.4173 | 5.5864 | 23.6409 | 8.0445 | 32.178 | 10.9494 | 42.0283 | 14.3013 | 55.1804 | 18.7767 | 72.4004 | 24.6362
[57 empty] | Filter AG | 22 | 12.25 | 2.1849 | 1.2166 | 2.8538 | 1.589 | 3.6118 | 2.0111 | 4.9161 | 2.7374 | 6.421 | 3.5753 | 10.0328 | 5.5864 | 14.4472 | 8.0445 | 19.6643 | 10.9494 | 25.684 | 14.3013 | 33.7214 | 18.7767 | 44.2447 | 24.6362
[57 empty] | MTM | 22 | 7.35 | 2.1849 | 0.72996 | 2.8538 | 0.95342 | 3.6118 | 1.2067 | 4.9161 | 1.6424 | 6.421 | 2.1452 | 10.0328 | 3.3519 | 14.4472 | 4.8267 | 19.6643 | 6.5697 | 25.684 | 8.5808 | 33.7214 | 11.266 | 44.2447 | 14.7817

## 2850 addtional infos
https://www.pentairaquaeurope.com/files/catalogue/2022/en/170/index.html#zoom=z
PNs
To choose the right configuration please refer to below table
Rotating side mount adapter 2850&2910
PN: 61415-20
https://www.pentairaquaeurope.com/files/catalogue/2022/en/203/index.html#zoom=z

## 3150 additional infos
https://www.pentairaquaeurope.com/files/catalogue/2022/en/184/index.html#zoom=z
PNs:
To choose the right configuration please refer to below table
Tank Adapt Assy 3150 Side Mount
PN: 18023
Tank adapt assy 3150 Top Mount
PN: 18024
https://www.pentairaquaeurope.com/files/catalogue/2022/en/187/index.html#zoom=z

## 2910 addtional infos
https://www.pentairaquaeurope.com/files/catalogue/2022/en/176/index.html#zoom=z
PNs
To choose the right configuration please refer to below table
Rotating side mount adapter 2850&2910
PN: 61415-20
https://www.pentairaquaeurope.com/files/catalogue/2022/en/203/index.html#zoom=z

## 3900 addtional infos
https://www.pentairaquaeurope.com/files/catalogue/2022/en/190/index.html#zoom=z
PNs:
To choose the right configuration please refer to below table
Tank adapt assy 3900 TM flanged 6”
PN: 18925
Tank adapt assy 3900 SM
PN:18926
Tank adapt assy 3900 TM threaded 6”
PN: 18041
https://www.pentairaquaeurope.com/files/catalogue/2022/en/192/index.html#zoom=z

## V250 additional infos
https://www.pentairaquaeurope.com/files/catalogue/2022/en/243/index.html#zoom=z
https://www.pentairaquaeurope.com/files/catalogue/2022/en/243/index.html#zoom=z
To choose the right configuration please refer to below table

## Magnum additional infos
https://www.pentairaquaeurope.com/files/catalogue/2022/en/97/index.html#zoom=z
Magnum connection & side mount adapter
PNs for filter
https://www.pentairaquaeurope.com/files/catalogue/2022/en/57/index.html#zoom=z
PNs for softening
https://www.pentairaquaeurope.com/files/catalogue/2022/en/58/index.html#zoom=z

## System Magnum Flow booster
Example of the softening system: Magnum 298 IT 764L for regeneration with service flow booster
Example of the softening system: Magnum 298 IT 764L for service with backwash flow booster

## Filter 3W valves addtional info
BACKWASH only
PN | Desription | Q-ty
SFE-BK201/05 | SFE BK CONTROLLER 2 EXT.PILOTS_201 | 1 pc
3 way valve and fittings size to be chosen:
3V-50BKFE/05 | 3-WAY VALVE D.50 BK | 2 pcs
Fittings options: | options:
494-A/05 | Kit fitting PVC 2 ¼”valve side > D.50 mm to be glued | 6 pcs needed
494-G/05 | Kit fitting brass 2 ¼”valve side > 2”male | 6 pcs needed
494-H/05 | Kit fitting PVC 2 ¼”valve side > 1 ½”female | 6 pcs needed
494-P/05 | Kit fitting brass 2 ¼”valve side > 1 ½”male | 6 pcs needed
3V-63BKFE/05 | 3-WAY VALVE D.63 BK | 2 pcs
Fittings options:
494-I/05 | Kit fitting PVC 2 ¾”valve side > 63 mm to be glued | 6 pcs needed
494-I1/05 | Kit fitting 2 ¾”brass valve side > 63 mm PVC | 6 pcs needed
494-I2/05 | Kit fitting 2 ¾”brass valve side > 2”PVC | 6 pcs needed
494-R/05 | Kit fitting 2 ¾”PVC valve side > 2”PVC | 6 pcs needed
3V-63BKFE/06 | 3-WAY VALVE D.63 BK SEA WATER | 2 pcs
Fittings options:
494-I/05 | Kit fitting PVC 2 ¾”valve side > 63 mm to be glued | 6 pcs needed
494-I1/05 | Kit fitting 2 ¾”brass valve side > 63 mm PVC | 6 pcs needed
494-I2/05 | Kit fitting 2 ¾”brass valve side > 2”PVC | 6 pcs needed
494-R/05 | Kit fitting 2 ¾”PVC valve side > 2”PVC | 6 pcs needed
Accessories |  |  | Notes
2220-A | PNEUMATIC TUBING | 15 m | the q-ty might change depend on the installation point
202-M | TAPPO INNESTO RAPIDO TUBO DA 6mm(RD) 10 | 1 pcs | plugs for not used pilots
BACKWASH + RAPID RINSE
PN | Desription | Q-ty
SFE-BK304/05 | 3 pilots SFE for 3 pos. fltr w/Aquamatic | 1 pc
3 way valve and fittings size to be chosen:
3V-63BKFE/05 | 3-WAY VALVE D.63 BK | 4 pcs
494-Z/05 | Blind closure DN50-3V-63 | 2 pcs needed
Fittings options:
494-I/05 | Kit fitting PVC 2 ¾”valve side > 63 mm to be glued | 10 pcs needed
494-I1/05 | Kit fitting 2 ¾”brass valve side > 63 mm PVC | 10 pcs needed
494-I2/05 | Kit fitting 2 ¾”brass valve side > 2”PVC | 10 pcs needed
494-R/05 | Kit fitting 2 ¾”PVC valve side > 2”PVC | 10 pcs needed
3V-63BKFE/06 | 3-WAY VALVE D.63 BK SEA WATER | 4 pcs
494-Z/05 | Blind closure DN50-3V-63 | 2 pcs needed
Fittings options:
494-I/05 | Kit fitting PVC 2 ¾”valve side > 63 mm to be glued | 10 pcs needed
494-I1/05 | Kit fitting 2 ¾”brass valve side > 63 mm PVC | 10 pcs needed
494-I2/05 | Kit fitting 2 ¾”brass valve side > 2”PVC | 10 pcs needed
494-R/05 | Kit fitting 2 ¾”PVC valve side > 2”PVC | 10 pcs needed
Accessories |  |  | Notes
2220-A | PNEUMATIC TUBING | 15 m | the q-ty might change depend on the installation point
202-M | TAPPO INNESTO RAPIDO TUBO DA 6mm(RD) 10 | 1 pcs | plugs for not used pilots